## 1. Introduction
|  | Workbook Contents |  | Introduction to the MBBR worksheets in this workbook:
Click on tabs at the bottom of the screen to access the following: |  |  |  | Two worksheets are provided to carry out basin sizing and aeration calculations as well as
alkalinity requirements for a Pre-Anoxic Denitrification process and for a Post-Anoxic
| Tab 1. Introduction (current tab) |  |  | Denitrification process. The worksheets include calculations for the BOD removal stage
and nitrification stage as well as for the anoxic tank.
Tab 2. Pre-Anoxic Denitrification
Basin sizing is based on a carrier surface area loading rate (SALR). For BOD removal and
| Tab 3. Post-Anoxic Denitrification |  |  | denitrification, the design SALR value is selected by the user based on the treatment
objective, (e.g. high rate BOD removal, normal rate BOD removal, or low rate BOD removal.
| Tab 4. Derivation of SARRmax vs D.O. Equation (for Nitrification) |  |  | Typical SALR values are provided on the worksheets. For nitrification, the design SALR is
calculated from a kinetic model based on the D.O. level to be maintained in the reactor
| Tab 5. Derivation of Saturation DO vs T Equation |  |  | and the target effluent ammonia nitrogen concentration.
Note that the estimated effluent concentration for BOD, or nitrate nitrogen from each
Why you shouldn’t give copies of this workbook away |  |  |  | BOD removal or denitrification stage is calculated by using an estimated value for the
We at EngineeringExcelTemplates.com hope that you find this workbook useful. If you |  |  |  | SARR/SALR (surface area removal rate/surface area loading rate). The estimated value
would like us to develop additional useful spreadsheets for you in the future, then encourage |  |  |  | for the SARR/SALR is based on an appropriate graph or table from one of the references
your friends and colleagues to buy their own copies, rather than allowing them to copy |  |  |  | as shown on the worksheets.
the spreadsheet you purchased. We have deliberately set our prices so low that no one
can really claim that they can’t afford to pay. But low prices will work for us—that is, we |  |  |  | The basin sizing calculations require values for several MBBR carrier properties: (specific
can stay in business—only if we can sell enough copies. Bottom line: the more you get |  |  |  | surface area in m2/m3 and % void space). Values to be used in the design calculations
other people to pay for their own copies, the more low-cost useful spreadsheets will be |  |  |  | should come from your carrier supplier.
available for you in the future.
The aeration/blower calculations are made for a coarse bubble diffuser system.
This workbook is provided "as is", without warranty of any kind, express or |  |  |  | Coarse bubble diffusers are typically used, because they work better
implied. |  |  |  | with the suspended carrier media.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2021 Harlan H. Bengtson. All Rights Reserved.

## 2. Pre-Anoxic Denitrif.
MBBR Process Design Calculations - U.S. units
Pre-Anoxic Denitrification Process
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
I. Wastewater Parameter Inputs
1. Parameters for All Three Stages
Design ww Flow Rate, Qo = |  | 0.2 | MGD |  | Prim. Effl. BOD, So = |  | 180 | mg/L
Prim. Effl. TKN Conc. = |  | 25 | mg/L |  | Prim. Effl. NO3-N Conc. = |  | 0 | mg/L | Estimation of SARR/SALR Ratio: Default data points for derivation of a SARR vs SALR
Peak Hour Factor = |  | 4 | Prim. Effl. Alkalinity = |  |  | 140 | mg/L as CaCO3 |  | equation are provided for The denitrification and BOD removal stages. They may be
replaced by values from user data if such data is available.
2. Parameters for First (Pre-Anoxic) Stage: | [13 empty] | NOTE: This graph was prepared using values from a similar graph in
[5 empty] | Data points for SARR/SALR vs SALR |  |  |  |  | Typical Design Values for Carrier Surface Loading Rate (SALR): |  |  |  | Rusten and Paulsrud's presentation (Ref #6 below).
Target Effl. NO3-N Conc. = |  | 9 | mg/L |  | SALR (g/m2/d): |  | 0.2 | 0.5 |  | (from References (2) below)
Est. of NO3-N Recycle Rato: |  | 1.4388 |  |  | SARR/SALR: |  | 0.95 | 0.94
(QR/Qo) - An estimate is needed here to start |  |  |  | (default values above are from a graph of Pre-Anoxic
the iterative calculation in Sec IV below |  |  |  | SARR vs SALR in ref #6 below right)
Design Value of NO3-N Surface |  |  |  | (The graph is shown at the right.)
Area Loading Rate (SALR) = |  | 0.9 | g/m2/d |  | Slope, SARR/SALR vs SALR: |  |  | -0.033333
See information on typical design |  |  |  |  | Intercept, SARR/SALR vs SALR: |  |  | 0.95667
values for SALR at right. |  |  |  |  | Est. of SARR/SALR Rato = |  |  | 0.92667
(Surf. Area Removal Rate/Surf. Area Loading Rate)
3. Parameters for Second (BOD Removal) Stage:
Data points for SARR/SALR vs SALR
Design Value of BOD Surface |  |  |  |  | SALR (g/m2/d): |  | 7.5 | 15
Area Loading Rate (SALR) = |  | 6 | g/m2/d |  | SARR/SALR: |  | 0.925 | 0.875
See information on typical design |  |  |  | (default values above are from the table of typical values
values for SALR at right. |  |  |  | of % BOD removal vs SALR shown at the right from ref #2)
Est. of SARR/SALR Rato = |  | 0.935 |  |  | Slope, SARR/SALR vs SALR: |  |  | -0.0066667
(Surf. Area Removal Rate/Surf. Area Loading Rate) |  |  |  |  | Intercept, SARR/SALR vs SALR: |  |  | 0.975
4. Parameters for Third (Nitrification) Stage:
Equations derived for SARRmax vs D.O. and NH4N @ SARRmax vs D.O.
Min Design Temp., T = |  | 45 | oF | Target Effl NH4-N Conc, NH4-Ne = |  |  | 4 | mg/L | on Worksheet 4 are:
[5 empty] | D.O Conc. in Reactor = |  | 3 | mg/L
[6 empty] | (beween 3.0 and 9.0 mg/L) |  |  | SARRmax = -0.0059(D.O.)2 + 0.2429(D.O.) + 0.1662
5. Preliminary Calculations - Design SALR value for Nitrification
NH4-Ne @ SARRmax = 0.0191*(D.O.)2 + 0.1287(D.O.) + 0.1921
% NH4-N removal = |  | 84% |  |  | NH4-Ne @ SARRmax = |  | 0.7501 | mg/L
Maximum SARR = |  | 0.8418 | g/m2/d | SARR @ NH4-Ne, 15oC, SARR15 = |  |  | 0.8418 | g/m2/d | SARR temperature correction coefficients being used are: q = 1.058 for DO limited
|  |  |  | SARR @ NH4-Ne, T oC, SARRT = |  |  | 0.54296 | g/m2/d | conditions and q = 1.098 for ammonia limited conditions. (per Salvetti et al - see ref list below)
SARR Temp. Coeff, q = |  | 1.058 | Design Value for nitrification SALR = |  |  |  | 0.64638 | g/m2/d | SARR temperature adjustments are made with: |  |  |  | SARRT = SARR15q(T - 15)
II. Determine whether to use Pre-Anoxic or Post-Anoxic Denitrification | [8 empty] | SALR is calculated as SARR/% removal.
Carbon:Nitrogen Ratio, C/N = |  | 7.2 |  | Use this Worksheet for Pre-Anoxic |  |  |  |  | Criteria for Determining whether to use Pre- or Post-Denitrification:
Target % N removal = |  | 64% |  | Denitrification calculations |  |  |  |  | (from references 1 and 2 below)
1. Pre-Denitirication is suitable if C/N > 4 and Target % Removal of N < 75%
III. Carrier and Tank Shape Parameter Inputs for all Three Stages
2. Post-Denitirication should be used if C/N < 4 or Target % Removal of N > 75%
Carrier Spec. Surf. Area = |  | 500 | m2/m3 | Click on green box and then on
(from carrier mfr/vendor) |  |  |  | arrow to Select Tank Shape: |  |  | rectangular
Liquid Depth in Tank = |  | 8 | ft |  | Carrier % Void Space = |  | 60%
Tank L:W ratio = |  | 1.5 |  |  | (from carrier mfr/vendor - only needed to
(target L:W - only used if tank is rectangular) |  |  |  |  | calculate hydraulic detention time)
IV. Calculation of Carrier Volume and Required Tank Volume & Dimensions
1. First Stage (Pre-Anoxic Tank) Calculations |  |  |  |  | (Carrier fill % is typically between 30% and 70%. Lower
values are more conservative, allowing future capacity
Design Carrier Fill % = |  | 40% | (for first stage) |  | expansion or reduction of SALR by adding more carrier.
NO3-N Daily Loading = |  | 21.6 | lb/day |  | Calculated Tank Volume = |  | 54.4308 | m3 | Equations used for Tank Sizing - Pre-Anoxic Stage
NO3-N Daily Loading = |  | 9797.544 | g/day |  |  |  | 1922.2056 | ft3
Carrier Surf. Area needed = |  | 10886.16 | m2 |  |  |  | 14378.0976 | gal | NO3-N Daily Loading = Qo*Prim Effl NO3-N*8.34 + Qo*NO3-N Recycle Ratio*Target Effl NO3-N*8.34
Calculated Carrier Volume = |  | 21.7723 | m3 |  | Calculated Tank Width = |  | 12.6564 | ft | Carrier Surf. Area needed = Nitrate Daily Loading*453.59/SALR_PreAnoxic
Tank Liquid Volume = |  | 1614.6527 | ft3 |  | Calculated Tank Length = |  | 18.9846 | ft | Carrier Volume needed = Carrier Surf Area/Carrier Spec Surf Area
|  |  |  | Nominal Hydraulic Retention Time at |  |  |  |  | Required Tank Volume = Carrier Volume/Des Carrier Fill PerCent
Estimate of NO3-N Surface Area |  |  |  |  | Design Average Flow = |  | 86.9587 | min | Tank Width & Length calculated from: Tank Volume = L*W*Liquid Depth
Removal Rate, SARR = |  | 0.834 | g/m2/d |  | Peak Hourly Flow = |  | 21.7397 | min | Or, Tank Diameter calculated from: Tank Volume = (pD2/4)Liquid Depth
Req'd NO3-N Removal Rate: |  | 20.016 | lb/day | Est. of NO3-N Removal Rate: |  |  | 20.016 | g/day
(for Effl. NO3-N = Target Value) |  |  |  | Est. Rem Rate - Req'd Rate: |  |  | 0 | g/day | Tank Liquid Volume = Tank Volume-((1-Carrier PerCent Void)*Carrier Volume)
NOTE: Use Excel's "Goal Seek" to find QR/Qo as follows: Place the cursor on cell H73 and click on | [8 empty] | Nominal HRT at Des Ave Flow = Tank Liq Vol/(WW Flow Rate/(24*60))
"Goal Seek" (in the "tools" menu of older versions and under "Data - What if Analysis" in newer | [8 empty] | Nominal HRT at Peak Hourly Flow = Hydr Det Time at Des Ave Flow/Peak Hour Factor
versions of Excel). Enter values to "Set cell:" H73, "To value:" 0, "By changing cell:" c17, and | [8 empty] | Estimated SARR = SALR(SARR/SALR)
click on "OK". The calculated value of QR/Qo will appear in cell C17 and cell H73 should equal zero | [8 empty] | Required NO3-N Removal Rate = Qo*(Prim Effl TKN - Effl N03-N - Effl NH3-N)*8.34
if the process worked properly. Note that an initial estimate of QR/Qo is needed in cell C17 to start | [8 empty] | Estimated NO3-N Removal Rate = SARR*Carrier Surf Area
the iterative process.
2. Second Stage (BOD Removal) Calculations |  |  |  |  | Est. of Effl BOD Conc.: |  | 10.8786 | mg/L
Equations used for Tank Sizing - BOD Removal Stage
Design Carrier Fill % = |  | 72.76% | (for second stage) |  | Calculated Tank Volume = |  | 58.0134 | m3
BOD Daily Loading = |  | 279.1619 | lb/day |  |  |  | 2048.7222 | ft3 | BOD Daily Loading = (Qo*So*8.34) + (Qo*Recycle Ratio*8.34*Se) - (0.67*(20/7)*NO3-N removal rate)
BOD Daily Loading = |  | 126625.0484 | g/day |  | Calculated Tank Width = |  | 13.0662 | ft | Carrier Surf. Area needed = BOD Daily Loading*453.59/SALR_BOD
Carrier Surf. Area needed = |  | 21104.1747 | m2 |  | Calculated Tank Length = |  | 19.5994 | ft | Carrier Volume needed, Required Tank Volume, and Tank dimensions
Calculated Carrier Volume = |  | 42.2083 | m3 | Nominal Hydraulic Retention Time at |  |  |  |  | use the same equations shown above.
Tank Liquid Volume = |  | 1452.4927 | ft3 |  | Design Average Flow = |  | 78.2254 | min
Estimate of BOD Surface Area |  |  |  |  | Peak Hourly Flow = |  | 19.5564 | min | Tank Liquid Volume, Nominal HRTs, and Estimated SARR are
Removal Rate, SARR = |  | 5.61 | g/m2/d | Calculated Effl BOD Conc.: |  |  | 10.8786 | mg/L | calculated as shown above.
Est. of BOD Removal Rate: |  | 118394.4202 | g/day |  | If the calculated Effl. BOD conc. Is too high, the |  |  |  | Estimated BOD Removal Rate = SARR*Carrier Surf Area
|  | 261.0164 | lb/day |  | design value of SALR (in cell C28) should be reduced. |  |  |  | Calculated Eff. BOD Conc. = (BOD Daily Loading - BOD Removal Rate)/Qo/8.34
|  |  | Estimated - Calculated Effl BOD Conc. = |  |  |  | 0 | mg/L
NOTE: Use Excel's "Goal Seek" to find BODe as follows: Place the cursor on cell H93 and click on | [8 empty] | NH3-N Daily Loading = Qo*Prim Effl NH3-N + Qo*Recycle Ratio*Effl NH3-N
"Goal Seek" (in the "tools" menu of older versions and under "Data - What if Analysis" in newer | [8 empty] | Equations used for Tank Sizing - Nitrification Stage
versions of Excel). Enter values to "Set cell:" H93, "To value:" 0, "By changing cell:" H81, and
click on "OK". The calculated value of BODe will appear in cell H81 and cell H93 should equal zero | [8 empty] | NH3-N Daily Loading = Qo*Prim Effl NH3-N*8.34 + Qo*Recycle Ratio*Effl NH3-N*8.34
if the process worked properly. Note that an initial estimate of BODe is needed in cell H82 to start | [8 empty] | Carrier Surf. Area needed = NH3-N Daily Loading*453.59/SALR_NH3-N
the iterative process. | [8 empty] | Carrier Volume needed, Required Tank Volume, and Tank dimensions
use the same equations shown above.
1st stage tank volume - 2nd stage tank volume = |  |  |  |  | -3.5826
To make the 2nd stage tank volume the same as the first stage tank volume, use | [8 empty] | Tank Liquid Volume, Nominal HRTs, and Estimated SARR are
Excel's Goal Seek process to set cell c94 equal to zero by changing the value in cell C83. | [8 empty] | calculated as shown above.
Estimated NH3-N Removal Rate = SARR*Carrier Surf Area
3. Third Stage (Nitrification) Calculations | [8 empty] | Calculated Eff. NH3-N Conc. = (NH3-N Daily Loading - NH3-N Removal Rate)/Qo/8.34
Design Carrier Fill % = |  | 60% | (for third stage) |  | Tank Liquid Volume = |  | 3220.6441 | ft3
NH3-N Daily Loading = |  | 51.3 | lb/day |  | Calculated Tank Volume = |  | 119.998 | m3 | Rules of Thumb for Estimating Oxygen/Air Requirements - Coarse Bubble Diffusers:
NH3-N Daily Loading = |  | 23269.167 | g/day |  |  |  | 4237.6896 | ft3 | Source:
Carrier Surf. Area needed = |  | 35999.4017 | m2 |  | Calculated Tank Width = |  | 18.792 | ft | http://www.xylemwatersolutions.com/scs/sweden/sv-se/produkter/cirkulationspumpar/documents/san3.pdf
Calculated Carrier Volume = |  | 71.9988 | m3 |  | Calculated Tank Length = |  | 28.1881 | ft
Estimate of NH3-N Surface Area |  |  |  | Nominal Hydraulic Retention Time at |  |  |  |  | 1. The typical AOR/SOR (or AOTE/SOTE) is 0.50 for a coarse bubble aertion system.
[5 empty] | Design Average Flow = |  | 173.451 | min |  |  | (or 0.33 for a fine bubble aeration system)
1st stage tank volume - |  |  |  |  | Peak Hourly Flow = |  | 43.3628 | min | 2. The typical SOTE is 0.75% per foot of diffuser submergence for a coarse bubble system
3rd stage tank volume = |  | -65.5672 | [7 empty] | (or 2.0 % per foot of diffuser submergence for a fine bubble system)
To make the 3rd stage tank volume the same as the first |  |  |  |  | Check on BOD SALR: |  | 0.22863 | g/m2/d | 3. Air weighs 0.075 lb/ft3 (1.20 kg/m3) and contains 23% oxygen by weight, thus:
stage tank volume, use Excel's Goal Seek process to set |  |  |  |  | (BOD SALR should be < 0.5 g/m2/d in order
cell C108 to zero by changing the value in cell C100. |  |  |  |  | to achieve a good nitrification rate) |  |  |  | 4. Air contains 0.0173 lbm of oxygen/ft3. (0.2770 kg of oxygen/m3)
V. Calculation of Oxygen/Air/Blower Requirements - BOD Removal Stage
5. For biological treatment with SRT fro 5 to 10 days, lb oxygen required /lb BOD removed
Inputs: (Values of "Rule of Thumb" Constants to be used in Calculations - See notes at right) | [8 empty] | is typically in the range from 0.92 - 1.1 lb O2/lb BOD. Higher SRT results in a higher value
of lb O2 required/lb BOD removed. (For a very high SRT, as is typical for an MBBR process,
O2 needed per lb BOD = |  | 1.5 | lb O2/lb BOD |  | Depth of Diffusers = |  | 7.5 | ft | this value would be about 1.5 lb O2/lb BOD removed.)
O2 needed per lb NH3-N = |  | 4.57 | lb O2/lb NH3-N |  | Standard Temperature = |  | 68 | oF
SOTE as Function of Depth = |  | 0.75% | % per ft depth |  | Standard Pressure = |  | 14.7 | psi | 6. The oxidation of 1 lb of ammonia nitrogen typically requires 4.1 to 4.6 lb of oxygen.
AOTE/SOTE = |  | 0.5 |  |  | Atmospheric Pressure = |  | 14.7 | psi
Press. Drop across Diffuser = |  | 12 | in W.C. |  | Air Density at STP = |  | 0.075 | lbm/SCF
(from mfr/vendor) |  |  |  |  | O2 Content in Air = |  | 0.0173 | lbm/SCF
Calculations:
Equations used for Oxygen/Air/Blower Calculations
Oxygen Requirement = |  | 418.7429 | lb/day |  |  | AOTE = | 2.812%
| SOTE = | 5.625% |  |  | Air Requirement = |  | 597.6491 | SCFM | Oxygen Requirement (lb/day) = Qo(4.57(NH4-No - NH4-Ne)*[(mg/L)/(lb/MG)]
Blower Outlet Pressure = |  | 18.3832 | psia
Pressure at Mid-Depth = Patm + [g4H2O(ddiff/2)]/144 in2/ft2
VI. Calculation of Oxygen/Air/Blower Requirements - Nitrification Stage
[9 empty] | AOTE = SOTE*a*F[(B(PD/Pstd)Cs - D.O.)/Css]q(tww - 20) |  |  |  | (Tww in oC)
Inputs:
Std O2 transf effic, SOTE = |  | 5.6% |  |  | Des. Barom. Press., Patm = |  | 14.5 | psi | SCFM = (lb/day O2/AOTE)*MWair/[O2 fract in air)(MWO2)(rair)(60 min/hr)(24 hr/day)]
(from diffuser mfr or vendor) |  |  |  |  | (ambient pressue at site)
Diffuser Fouling Factor, F = |  | 0.8 |  |  | Ratio of D.O. saturation in WW to that in clean |  |  |  | ACFM = SCFM[(Tww + 459.67)/(Tstd + 459.67)](Pstd/PB2)
Ratio of oxygen transfer rate in wastewater |  |  |  |  | water at same T & P, B = |  | 1
to that in clean water, a = |  | 0.6 |  |  | Pressure drop across |  |  |  | PB2 = Patm + DPdiff(0.036126 psi/in H2O) + gH2O*ddiff/144 in2/ft2
Depth of diffuser, ddiff = |  | 7.5 | ft |  | diffuser, DPdiff = |  | 12 | in H2O
Std. Air Density, rair = |  | 0.07521 | lb/ft3 |  | (from diffuser mfr or vendor)
References for additional background information:
Calculations
1. Odegaard, Hallvard, "Compact Wastewater Treatment with MBBR." DSD International Conference
Oxygen Requirement = |  | 160.078 | lb/day |  | Act O2 transf effic, AOTE = |  | 2.218% |  | Hong Kong, 12. 11-14-2014. |  |  | http://www.dsdic2014.hk/ppt/Presentation_(B4-1).pdf
Pressure at mid Depth, PD = |  | 16.125 | psi |  | Des. Air Flow Rate, SCFM = |  | 288.6009 | SCFM
D.O sat'n conc. for clean water at ww |  |  |  |  | Des. Air Flow Rate, ACFM = |  | 223.1425 | ACFM | 2. Odegaard, H., "The Moving Bed Biofilm Reactor," in Igasrashi, T, Watanabe, Y., Asano, T. and
temp. and 1 atm, Cs = |  | 12.0764 | mg/L | Blower Outlet Pressure, PB2 = |  |  | 18.1835 | psi | Tambo, N., Water Environmental Engineering and Reuse of Water, Hokkaido Press 1999, p 250-305.
(Derivation of equation for sat'n D.O. vs T is shown on worksheet 4) | [8 empty] | http://netedu.xauat.edu.cn/jpkc/netedu/jpkc2009/szylyybh/content/wlzy/7/3/The%20Moving%20Bed%20Biofilm%20Reactor.pdf
VII. Calculation of Alkalinity Requirements | [8 empty] | 3. Steichen & Phillips, H., M, Black & Veach, Process and Practical Design Considerations for
Input: | Target Effluent Alkalinity = |  |  |  | 80 | mg/L |  |  | IFAS and MBBR Technologies, Headworks International Presentation, 03/18/2010
http://www.headworksinternational.com/userfiles/file/Webinar/BV_Webinar_Slides.pdf
Constants needed for Calculations:
4. McQuarrie, J.P. and Boltz, J.P., Moving Bed Biofilm Reactor Technology: Process Applications,
Equiv Wt. of CaCO3 = |  | 50 | g/equiv. |  | Equiv Wt. of NaHCO3 = |  | 84 | g/equiv. | Design and Performance, Water Environment Research, Vol 83, No. 6. June 2011.
Alkalinity used for Nitrification = |  |  | 7.14 | g CaCO3/g NH3-N removed |  |  |  |  | 5. Bjornberg, Corey, "Moving Bed Biofilm Reactor for Nitrification/Denitrification"
Alkalinity produced by Denitrification = |  |  | 3.57 | g CaCO3/g NO3-N removed |  |  |  |  | https://www.ndsu.edu/pubweb/nrg/outreach/Moving%20Bed%20Biofilm%20Reactor%20for%20Denitrification%20Corey.pdf
Calculations | [8 empty] | 6. Rusten, B. and Paulsrud, B., Improved Nutrient Removal with Biofilm Reactors,
Aquateam - Norwegian Water Technology Center, Oslo, Norway.
Alkalinity to be added = |  |  | 32.82 | mg/L as CaCO3
Daily Alkalinity Requirement = |  |  | 54.7438 | lb/day as CaCO3 |  |  |  |  | 7. Metcalf & Eddy, "Wastewater Engineering Treatment and Resource Recovery", 5th Ed, McGraw-Hill, 2014
For sodium bicarbonate use to add alkalinity: | [8 empty] | 8. Salvetti, R., A. Azzellino, R. Canziani, and L. Bonomo (2006), "Effect of Temperature on Tertiary
Nitrification in Moving-Bed Biofilm Reactors," Water Res., 40, 15, 298-2993.
Daily NaHCO3 Requirement = |  |  | 91.9695 | lb/day NaHCO3
[9 empty] | 9. Bengtson, Harlan H., | Spreadsheets for MBBR Denitrification Design Calculations,
an Amazon Kindle ebook.
| Find more Excel spreadsheets for engineering at | [7 empty] | 10. Bengtson, Harlan H., | Spreadsheets for MBBR Process Design Calculations,
|  | EngineeringExcelTemplates.com | [6 empty] | available as a paperback book and as an Amazon Kindle ebook.
[9 empty] | 11. Bengtson, Harlan H., | Biological Wastewater Treatment Process Design Calculations
| Copyright © 2021 Harlan H. Bengtson. All Rights Reserved. | [7 empty] | available as a paperback book and as an Amazon Kindle ebook.
cylindrical
rectangular
2
3
4
5
6
9

## 3. Post-Anoxic Denitrif
MBBR Process Design Calculations - U.S. units
Post-Anoxic Denitrification Process
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
I. Wastewater Parameter Inputs
1. Parameters for All Three Stages
Design ww Flow Rate, Qo = |  | 0.2 | MGD |  | Prim. Effl. BOD, So = |  | 180 | mg/L
Prim. Effl. TKN Conc. = |  | 35 | mg/L |  | Prim. Effl. NO3-N Conc. = |  | 0 | mg/L | Estimation of SARR/SALR Ratio: Default data points for derivation of a SARR vs SALR
Peak Hour Factor = |  | 4 | Prim. Effl. Alkalinity = |  |  | 140 | mg/L as CaCO3 |  | equation are provided for The denitrification and BOD removal stages. They may be
replaced by values from user data if such data is available.
2. Parameters for First (BOD Removal) Stage:
[5 empty] | Data points for SARR/SALR vs SALR |  |  |  | Typical Design Values for Carrier Surface Loading Rate (SALR):
Design Value of BOD Surface |  |  |  |  | SALR (g/m2/d): |  | 7.5 | 15 | (from Reference (2) below)
Area Loading Rate (SALR) = |  | 6 | g/m2/d |  | SARR/SALR: |  | 0.925 | 0.875
See information on typical design |  |  |  | (default values above are from the table of typical values
values for SALR at right. |  |  |  | of % BOD removal vs SALR shown at the right from ref #2)
Est. of SARR/SALR Rato = |  | 0.935
(Surf. Area Removal Rate/Surf. Area Loading Rate) |  |  |  |  | Slope, SARR/SALR vs SALR: |  |  | -0.0066667
[5 empty] | Intercept, SARR/SALR vs SALR: |  |  | 0.975
3. Parameters for Second (Nitrification) Stage:
Influent NH4-N Conc. = |  | 25 | mg/L | Target Effl NH4-N Conc, NH4-Ne = |  |  | 3.3 | mg/L
Min Design Temp., T = |  | 45 | oF |  | D.O Conc. in Reactor = |  | 3 | mg/L | Equations derived for SARRmax vs D.O. and NH4N @ SARRmax vs D.O.
[6 empty] | (beween 3.0 and 9.0 mg/L) |  |  | on Worksheet 4 are:
4. Preliminary Calculations - Design Nitrification SALR value
SARRmax = -0.0059(D.O.)2 + 0.2429(D.O.) + 0.1662
% NH4-N removal = |  | 86.8% |  |  | NH4-Ne @ SARRmax = |  | 0.7501 | mg/L
Maximum SARR = |  | 0.8418 | g/m2/d | SARR @ NH4-Ne, 15oC, SARR15 = |  |  | 0.8418 | g/m2/d | NH4-Ne @ SARRmax = 0.0191*(D.O.)2 + 0.1287(D.O.) + 0.1921
|  |  |  | SARR @ NH4-Ne, T oC, SARRT = |  |  | 0.54296 | g/m2/d
SARR Temp. Coeff, q = |  | 1.058 | Design Value for nitrification SALR = |  |  |  | 0.62553 | g/m2/d | SARR temperature correction coefficients being used are: q = 1.058 for DO limited
conditions and q = 1.098 for ammonia limited conditions. (per Salvetti et al - see ref list below)
5. Parameters for Third (Post-Anoxic) Stage: | [8 empty] | SARR temperature adjustments are made with: |  |  |  | SARRT = SARR15q(T - 15)
[5 empty] | Data points for SARR/SALR vs SALR |  |  |  | SALR is calculated as SARR/% removal.
Target Effl. NO3-N Conc. = |  | 4 | mg/L |  | SALR (g/m2/d): |  | 1 | 1.8
Design Value of BOD Surface |  |  |  |  | SARR/SALR: |  | 0.9 | 0.88889
Area Loading Rate (SALR) = |  | 2 | g/m2/d |  | (default values above are from a graph of
See information on typical design |  |  |  |  | Post-Anoxic SARR vs SALR in ref #6 below right)
values for SALR at right. |  |  |  |  | (The graph is shown at the right.)
Est. of SARR/SALR Rato = |  | 0.88611 |  |  | Slope, SARR/SALR vs SALR: |  |  | -0.013889
(Surf. Area Removal Rate/Surf. Area Loading Rate) |  |  |  |  | Intercept, SARR/SALR vs SALR: |  |  | 0.91389
II. Determine whether to use Pre-Anoxic or Post-Anoxic Denitrification
Carbon:Nitrogen Ratio, C/N = |  | 5.1429 |  | Use this Worksheet for Post-Anoxic
Target % N removal = |  | 88.57% |  | Denitrification calculations |  |  |  |  | NOTE: This graph was prepared using values from a similar graph in
Rusten and Paulsrud's presentation (Ref #6 below).
III. Carrier and Tank Shape Parameter Inputs for all Three Stages
Criteria for Determining whether to use Pre- or Post-Denitrification:
Carrier Spec. Surf. Area = |  | 500 | m2/m3 | Click on green box and then on |  |  |  |  | (from references 1 and 2 below)
(from carrier mfr/vendor) |  |  |  | arrow to Select Tank Shape: |  |  | rectangular
Liquid Depth in Tank = |  | 8 | ft |  | Carrier % Void Space = |  | 60% |  | 1. Pre-Denitirication is suitable if C/N > 4 and Target % Removal of N < 75%
Tank L:W ratio = |  | 1.5 |  |  | (from carrier mfr/vendor - only needed to
(target L:W - only used if tank is rectangular) |  |  |  |  | calculate hydraulic detention time) |  |  |  | 2. Post-Denitirication should be used if C/N < 4 or Target % Removal of N > 75%
IV. Calculation of Carrier Volume and Required Tank Volume & Dimensions | [8 empty] | Equations used for Tank Sizing - BOD Removal Stage
1. First Stage (BOD Removal) Calculations |  |  |  |  | (Carrier fill % is typically between 30% and 70%. Lower |  |  |  | BOD Daily Loading = (Qo*So*8.34)
[5 empty] | values are more conservative, allowing future capacity |  |  |  | Carrier Surf. Area needed = BOD Daily Loading*453.59/SALR_BOD
Design Carrier Fill % = |  | 60% | (for first stage) |  | expansion or reduction of SALR by adding more carrier. |  |  |  | Carrier Volume needed = Carrier Surf Area/Carrier Spec Surf Area
BOD Daily Loading = |  | 300.24 | lb/day |  | Required Tank Volume = |  | 75.6588 | m3 | Required Tank Volume = Carrier Volume/Des Carrier Fill PerCent
BOD Daily Loading = |  | 136185.8616 | g/day |  |  |  | 2671.8657 | ft3 | Tank Width & Length calculated from: Tank Volume = L*W*Liquid Depth
Carrier Surf. Area needed = |  | 22697.6436 | m2 |  |  |  | 19985.5557 | gal | Or, Tank Diameter calculated from: Tank Volume = (pD2/4)Liquid Depth
Calculated Carrier Volume = |  | 45.3953 | m3 |  | Calculated Tank Width = |  | 14.9216 | ft
Tank Liquid Volume = |  | 2030.6413 | ft3 |  | Calculated Tank Length = |  | 22.3825 | ft | Tank Liquid Volume = Tank Volume-((1-Carrier PerCent Void)*Carrier Volume)
|  |  |  | Nominal Hydraulic Retention Time at |  |  |  |  | Nominal HRT at Des Ave Flow = Tank Liq Vol/(WW Flow Rate/(24*60))
Estimate of BOD Surface Area |  |  |  |  | Design Average Flow = |  | 109.3622 | min | Nominal HRT at Peak Hourly Flow = Hydr Det Time at Des Ave Flow/Peak Hour Factor
Removal Rate, SARR = |  | 5.61 | g/m2/d |  | Peak Hourly Flow = |  | 27.3406 | min | Estimated SARR = SALR(SARR/SALR)
Est. of BOD Removal Rate: |  | 127333.7806 | g/day | Calculated Effl BOD Conc.: |  |  | 11.7 | mg/L | Estimated BOD Removal Rate = SARR*Carrier Surf Area
|  | 280.7244 | lb/day | If the calculated Effl. BOD conc. Is too high, the |  |  |  |  | Calculated Eff. BOD Conc. = (BOD Daily Loading - BOD Removal Rate)/Qo/8.34
design value of SALR (in cell C17) should be reduced.
2. Second Stage (Nitrification) Calculations | [8 empty] | Equations used for Tank Sizing - Nitrification Stage
Design Carrier Fill % = |  | 70% | (for second stage) Tank Liquid Volume = |  |  |  | 3075.4465 | ft3 | NH3-N Daily Loading = Qo*Prim Effl NH3-N*8.34
NH3-N Daily Loading = |  | 58.38 | lb/day |  | Required Tank Volume = |  | 120.9524 | m3 | Carrier Surf. Area needed = NH3-N Daily Loading*453.59/SALR_NH3-N
NH3-N Daily Loading = |  | 26480.5842 | g/day |  |  |  | 4271.3928 | ft3 | Carrier Volume needed, Required Tank Volume, and Tank dimensions
Carrier Surf. Area needed = |  | 42333.3315 | m2 |  |  |  | 31950.0185 | gal | use the same equations shown above.
Calculated Carrier Volume = |  | 84.6667 | m3 |  | Calculated Tank Width = |  | 18.8666 | ft
[5 empty] | Calculated Tank Length = |  | 28.2999 | ft | Tank Liquid Volume, Nominal HRTs, and Estimated SARR are
1st stage tank volume - |  |  |  | Nominal Hydraulic Retention Time at |  |  |  |  | calculated as shown above.
- 2nd stage tank volume = |  | -45.2936 |  |  | Design Average Flow = |  | 165.6312 | min | Estimated NH3-N Removal Rate = SARR*Carrier Surf Area
To make the 2nd stage tank volume the same as the |  |  |  |  | Peak Hourly Flow = |  | 41.4078 | min | Calculated Eff. NH3-N Conc. = (NH3-N Daily Loading - NH3-N Removal Rate)/Qo/8.34
first stage, use Excel's Goal Seek process to set cell
C83 equal to zero by changing the value in cell C76. |  |  |  |  | Check on BOD SALR: |  | 0.2091 | g/m2/d
(BOD SALR should be < 0.5 g/m2/d in order
3. Third Stage (Post-Anoxic) Calculations |  |  |  |  | to achieve a good nitrification rate) |  |  |  | Equations used for Tank Sizing - Post-Anoxic Stage
Design Carrier Fill % = |  | 31.7% | (for third stage) Required Tank Volume = |  |  |  | 75.6582 | m3 | NO3-N Daily Loading = Qo*Prim Effl NO3-N*8.34
NO3-N Daily Loading = |  | 52.8756 | lb/day |  | Tank Liquid Volume = |  | 2671.8424 | ft3 | Carrier Surf. Area needed = Nitrate Daily Loading*453.59/SALR_PreAnoxic
NO3-N Daily Loading = |  | 23983.8434 | g/day |  |  |  | 19985.3811 | gal | Carrier Volume needed, Required Tank Volume, and Tank dimensions
Carrier Surf. Area needed = |  | 11991.9217 | m2 |  | Calculated Tank Width = |  | 14.9216 | ft | use the same equations shown above.
Calculated Carrier Volume = |  | 23.9838 | m3 |  | Calculated Tank Length = |  | 22.3824 | ft
Tank Liquid Volume = |  | 2333.0622 | ft3 | Nominal Hydraulic Retention Time at |  |  |  |  | Tank Liquid Volume, Nominal HRTs, and Estimated SARR are
Estimate of NO3-N Surface Area |  |  |  |  | Design Average Flow = |  | 125.6494 | min | calculated as shown above.
Removal Rate, SARR = |  | 1.7722 | g/m2/d |  | Peak Hourly Flow = |  | 31.4123 | min | Required NO3-N Removal Rate = Qo*(Prim Effl TKN - Effl N03-N - Effl NH3-N)*8.34
Est. of NO3-N Removal Rate: |  | 21252.3501 | g/day | Calculated Effl NO3-N Conc.: |  |  | 3.6103 | mg/L | Estimated NO3-N Removal Rate = SARR*Carrier Surf Area
|  | 46.8537 | lb/day |  | If the calculated Effl. NO3-N conc. Is |  |  |  | Calculated Eff. NO3-N Conc. = (NO3-N Daily Loading - NO3-N Removal Rate)/Qo/8.34
1st stage tank volume - |  |  |  |  | too high, the design value of SALR
3rd stage tank volume = |  | 0.00066075 |  |  | (in cell C36) should be reduced.
To make the 3rd stage tank volume the same as the first | [8 empty] | Rules of Thumb for Estimating Oxygen/Air Requirements - Coarse Bubble Diffusers:
stage tank volume, use Excel's Goal Seek process to set | [8 empty] | Source:
cell C101 equal to zero by changing the value in cell C90. | [8 empty] | http://www.xylemwatersolutions.com/scs/sweden/sv-se/produkter/cirkulationspumpar/documents/san3.pdf
V. Calculation of Oxygen/Air/Blower Requirements - BOD Removal Stage | [8 empty] | 1. The typical AOR/SOR (or AOTE/SOTE) is 0.50 for a coarse bubble aertion system.
(or 0.33 for a fine bubble aeration system)
1. Inputs: (Values of "Rule of Thumb" Constants to be used in Calculations - See notes at right) | [8 empty] | 2. The typical SOTE is 0.75% per foot of diffuser submergence for a coarse bubble system
(or 2.0 % per foot of diffuser submergence for a fine bubble system)
O2 needed per kg BOD = |  | 1.5 | lb O2/lb BOD |  | Depth of Diffusers = |  | 7.5 | ft | 3. 1 SCF of air weighs 0.075 lb/ft3 and contains 23% oxygen by weight, thus:
SOTE as Function of Depth = |  | 0.75% | % per ft depth |  | Standard Temperature = |  | 68 | oF
AOTE/SOTE = |  | 0.5 |  |  | Standard Pressure = |  | 14.7 | psi | 4. 1 SCF of air contains 0.0173 lbm of oxygen.
Press. Drop across Diffuser = |  | 12 | in W.C. |  | Atmospheric Pressure = |  | 14.7 | psi
(from mfr/vendor) |  |  |  |  | Air Density at STP = |  | 0.075 | lbm/SCF | 5. For biological treatment with SRT from 5 to 10 days, lb oxygen required /lb BOD removed
[5 empty] | O2 Content in Air = |  | 0.0173 | lbm/SCF | is typically in the range from 0.92 - 1.1 lb O2/lb BOD. Higher SRT results in a higher value
Calculations | [8 empty] | of lb O2 required/lb BOD removed. (For a very high SRT, as is typical for an MBBR process,
this value would be about 1.5 lb O2/lb BOD removed.)
Oxygen Requirement = |  | 450.36 | lb/day |  |  | AOTE = | 2.812%
| SOTE = | 5.625% |  |  | Air Requirement = |  | 642.7746 | SCFM | 6. The oxidation of 1 lb of ammonia nitrogen typically requires 4.1 to 4.6 lb of oxygen.
Blower Outlet Pressure = |  | 18.3832 | psia
VI. Calculation of Oxygen/Air/Blower Requirements - Nitrification Stage
Inputs:
Equations used for Oxygen/Air/Blower Calculations
Std O2 transf effic, SOTE = |  | 5.6% |  |  | Des. Barom. Press., Patm = |  | 14.5 | psi
(from diffuser mfr or vendor) |  |  |  |  | (ambient pressue at site) |  |  |  | Oxygen Requirement (lb/day) = Qo(4.57(NH4-No - NH4-Ne)*[(mg/L)/(lb/MG)]
Diffuser Fouling Factor, F = |  | 0.8 |  |  | Ratio of D.O. saturation in WW to that in clean
Ratio of oxygen transfer rate in wastewater |  |  |  |  | water at same T & P, B = |  | 1 |  | Pressure at Mid-Depth = Patm + [g4H2O(ddiff/2)]/144 in2/ft2
to that in clean water, a = |  | 0.6 |  |  | Pressure drop across
Depth of diffuser, ddiff = |  | 7.5 | ft |  | diffuser, DPdiff = |  | 12 | in H2O | AOTE = SOTE*a*F[(B(PD/Pstd)Cs - D.O.)/Css]q(tww - 20)
Std. Air Density, rair = |  | 0.07521 | lb/ft3 |  | (from diffuser mfr or vendor)
SCFM = (lb/day O2/AOTE)*MWair/[O2 fract in air)(MWO2)(rair)(60 min/hr)(24 hr/day)]
Calculations
ACFM = SCFM[(Tww + 459.67)/(Tstd + 459.67)](Pstd/PB2)
Oxygen Requirement = |  | 165.4139 | lb/day |  | Act O2 transf effic, AOTE = |  | 2.218%
Pressure at mid Depth, PD = |  | 16.125 | psi |  | Des. Air Flow Rate, SCFM = |  | 298.2209 | SCFM | PB2 = Patm + DPdiff(0.036126 psi/in H2O) + gH2O*ddiff/144 in2/ft2
D.O sat'n conc. for clean water at ww |  |  |  |  | Des. Air Flow Rate, ACFM = |  | 230.5806 | ACFM
temp. and 1 atm, Cs = |  | 12.0764 | mg/L | Blower Outlet Pressure, PB2 = |  |  | 18.1835 | psi
(Derivation of equation for sat'n D.O. vs T is shown on worksheet 4)
References for additional background information:
VII. Calculation of Alkalinity Requirements
1. Odegaard, Hallvard, "Compact Wastewater Treatment with MBBR." DSD International Conference
Input: | Target Effluent Alkalinity = |  |  |  | 80 | mg/L as CaCO3 |  |  | Hong Kong, 12. 11-14-2014. |  |  | http://www.dsdic2014.hk/ppt/Presentation_(B4-1).pdf
Constants needed for Calculations: | [8 empty] | 2. Odegaard, H., "The Moving Bed Biofilm Reactor," in Igasrashi, T, Watanabe, Y., Asano, T. and
Tambo, N., Water Environmental Engineering and Reuse of Water, Hokkaido Press 1999, p 250-305.
Equiv Wt. of CaCO3 = |  | 50 | g/equiv. |  | Equiv Wt. of NaHCO3 = |  | 84 | g/equiv. | http://netedu.xauat.edu.cn/jpkc/netedu/jpkc2009/szylyybh/content/wlzy/7/3/The%20Moving%20Bed%20Biofilm%20Reactor.pdf
Alkalinity used for Nitrification = |  |  | 7.14 | g CaCO3/g NH3-N removed |  |  |  |  | 3. Steichen & Phillips, H., M, Black & Veach, Process and Practical Design Considerations for
Alkalinity produced by Denitrification = |  |  | 3.57 | g CaCO3/g NO3-N removed |  |  |  |  | IFAS and MBBR Technologies, Headworks International Presentation, 03/18/2010
http://www.headworksinternational.com/userfiles/file/Webinar/BV_Webinar_Slides.pdf
Calculations
4. McQuarrie, J.P. and Boltz, J.P., Moving Bed Biofilm Reactor Technology: Process Applications,
Alkalinity to be added = |  |  | 54.2767 | mg/L as CaCO3 |  |  |  |  | Design and Performance, Water Environment Research, Vol 83, No. 6. June 2011.
Daily Alkalinity Requirement = |  |  | 90.5335 | lb/day as CaCO3
5. Bjornberg, Corey, "Moving Bed Biofilm Reactor for Nitrification/Denitrification"
For sodium bicarbonate use to add alkalinity: | [8 empty] | https://www.ndsu.edu/pubweb/nrg/outreach/Moving%20Bed%20Biofilm%20Reactor%20for%20Denitrification%20Corey.pdf
Daily NaHCO3 Requirement = |  |  | 152.0963 | lb/day NaHCO3 |  |  |  |  | 6. Rusten, B. and Paulsrud, B., Improved Nutrient Removal with Biofilm Reactors,
Aquateam - Norwegian Water Technology Center, Oslo, Norway.
VII. Calculation of Carbon Source Requirements
Source for information about Carbon Sources for Denitrification and Required Dosages:
Inputs: | Carbon Source to be used: |  |  |  | Methanol |  |  |  | https://www.werf.org/c/KnowledgeAreas/NutrientRemoval/compendium/05-Tertiary_Denitrification_Processes.aspx
| COD Requirement for Denitrification = |  |  |  | 4.6 | lb COD/lb NO3-N removed
| COD Content of Carbon Source = |  |  |  | 1.5 | lb COD/lb Carbon Source |  |  | 7. Metcalf & Eddy, "Wastewater Engineering Treatment and Resource Recovery", 5th Ed, McGraw-Hill, 2014
Calculations | [8 empty] | 8. Salvetti, R., A. Azzellino, R. Canziani, and L. Bonomo (2006), "Effect of Temperature on Tertiary
Nitrification in Moving-Bed Biofilm Reactors," Water Res., 40, 15, 298-2993.
Carbon Source Dosage = |  |  | 3.0667 | lb Carbon Source/lb NO3-N removed
Daily Carbon Source Requirement = |  |  | 143.6845 | lb/day |  |  |  |  | 9. Bengtson, Harlan H., | Spreadsheets for MBBR Denitrification Design Calculations,
an Amazon Kindle ebook.
[9 empty] | 10. Bengtson, Harlan H., | Spreadsheets for MBBR Process Design Calculations,
available as a paperback book and as an Amazon Kindle ebook.
Find more Excel spreadsheets for engineering at
|  | EngineeringExcelTemplates.com | [6 empty] | 11. Bengtson, Harlan H., | Biological Wastewater Treatment Process Design Calculations
available as a paperback book and as an Amazon Kindle ebook.
Copyright © 2021 Harlan H. Bengtson. All Rights Reserved.
cylindrical
rectangular
2
3
4
5
6
9

## 4. SARRmax vs D.O.
Nitrification SARR:
Nitrification SARR:
|  |  | D.O. | SARRmax | N @ SARRmax
|  |  | mg/L | g/m2/d | mg/L
|  |  | 2 | 0.61 | 0.5
|  |  | 3 | 0.88 | 0.8
|  |  | 4 | 1.03 | 1
|  |  | 5 | 1.23 | 1.3
|  |  | 6 | 1.41 | 1.65
|  |  | 9 | 1.88 | 2.9
Adapted from Metcalf & Eddy, 5th Ed, Fig 9-25
The values in the table above for D.O. = 2 mg/L to 6 mg/Lcome from Figure 9-25
in Metcalf & Eddy, Wastewater Engineering, Treatment and Resource Recovery, 5th Ed.
The values for D.O. = 9 mg/L are from Odegaard, 1999 (reference shown below)
The N values at SARRmax were read from Figure 9-25 (or Odegaard, 1999).
The SARRmax values were calculated for those N values using Eqn 9-48 from Metcalf & Eddy,
5th Ed: SARR = [N/(2.2 + N)]*3.3, where N is the bulk liquid (effluent)
NH4-N concentration.
2. Odegaard, H., "The Moving Bed Biofilm Reactor," in Igasrashi, T, Watanabe, Y., Asano, T. and
Tambo, N., Water Environmental Engineering and Reuse of Water, Hokkaido Press 1999, p 250-305.
http://netedu.xauat.edu.cn/jpkc/netedu/jpkc2009/szylyybh/content/wlzy/7/3/The%20Moving%20Bed%20Biofilm%20Reactor.pdf
| D.O. | SARRmax
| mg/L | g/m2/d
| 2 | 0.61
| 3 | 0.88
| 4 | 1.03
| 5 | 1.23
| 6 | 1.41
| 9 | 1.88
SARRmax = -0.0059(D.O.)2 + 0.2429(D.O.) + 0.1662
(NH4-N)e @ SARRmax = 0.0191*(D.O.)2 + 0.1287(D.O.) + 0.1921
| D.O. | N @ SARRmax
| mg/L | mg/L
| 2 | 0.5
| 3 | 0.8
| 4 | 1
| 5 | 1.3
| 6 | 1.65
| 9 | 2.9

## 5. Satn DO vs T
Derivation of Equation for Saturation DO Concentration at WW Temperature:
Sat'n DO
T, oF | mg/L
35 | 13.96
36 | 13.75
37 | 13.54
38 | 13.34
39 | 13.15
40 | 12.96
41 | 12.77
42 | 12.59
43 | 12.41
44 | 12.24
45 | 12.07
46 | 11.91
47 | 11.75
48 | 11.59
49 | 11.44
50 | 11.29
51 | 11.14
52 | 11
53 | 10.86
54 | 10.72
55 | 10.59
56 | 10.46 | Source for DO vs T data: USGS website at:
57 | 10.33
58 | 10.21 |  | http://water.usgs.gov/software/DOTABLES/
59 | 10.08
60 | 9.96
61 | 9.85
62 | 9.73
63 | 9.62
64 | 9.51
65 | 9.4
66 | 9.3
67 | 9.19
68 | 9.09
69 | 8.99
70 | 8.9
71 | 8.8
72 | 8.71
73 | 8.61
74 | 8.52
75 | 8.44
76 | 8.35
77 | 8.26
78 | 8.18
79 | 8.1
80 | 8.02